23 81 29 VARIABLE REFRIGERANT VOLUME HVAC SYSTEM

- GENERAL

  - SECTION INCLUDES

    - Variable refrigerant volume HVAC system includes:

      - Outdoor/Condensing unit(s):

        - Size Range: 2 to 5 Tons Nominal

        - Daikin Model Numbers:

| RXSQ24TBVJ* RXSQ36TBVJ* |  |
| --- | --- |
| RXSQ48TBVJ* |  |
| RXSQ60TBVJ* |  |

      - Indoor Units

        - Input information as required

  - RELATED REQUIREMENTS

    - N/A

  - REFERENCES

    - N/A

  - SUBMITTALS

    - N/A

  - QUALITY ASSURANCE

    - MANUFACTURER QUALIFICATIONS:

      - The units shall be tested by a National Recognized Testing Laboratory (NRTL), in accordance with ANSI/UL 1995 – Heating and Cooling Equipment and bear the Listed Mark.

      - All wiring shall be in accordance with the National Electric Code (NEC).

      - Each combination shall be rated in accordance with Air Conditioning, Heating and Refrigeration Institutes’ (AHRI) Standard 210/240 and bear the AHRI label.

      - The system will be produced in an ISO 9001 and ISO 14001 facility, which are standards set by the International Standard Organization (ISO).  The system shall be factory tested for safety and function.

      - The condensing unit will be factory charged with R410A.

  - DELIVERY, STORAGE AND HANDLING

    - Unit shall be stored and handled according to the manufacturer’s recommendations.

  - WARRANTY

    - STANDARD LIMITED WARRANTY

      - Complete warranty details available from your local Daikin representative or at www.daikincomfort.com.

      - Daikin Comfort Technologies North America, Inc. warrants original owner of the non-residential building, multifamily residence or residence in which the Daikin products are installed that under normal use and maintenance for comfort cooling and conditioning applications such products (the “Products”) will be free from defects in material and workmanship. This warranty applies to compressor and all parts and is limited in duration to ten (10) years starting from the ‘’installation date’’ which is one of the two dates below:

        - The installation date is the date that the unit is originally commissioned, but no later than 18 months after the manufacture date noted on the unit’s rating plate.

        - If the date the unit is originally commissioned cannot be verified, the installation date is three months after the manufacture date.

- PRODUCTS

  - MANUFACTURERS

    - DESIGN BASIS:

      - The HVAC equipment basis of design is Daikin Comfort Technologies.  All bidders shall furnish the minimum system standards as defined by the base bid model numbers, model families or as otherwise specified herein (see Appendix A HVAC Equipment Alternate General Information).  In any event, the contractor shall be responsible for all specified items and intents of this document without further compensation.

  - HVAC SYSTEM DESIGN

    - SYSTEM DESCRIPTION:

      - The variable capacity heat pump air conditioning system shall be a Daikin Variable Refrigerant Volume Series (heat or cool model) split system.

      - The system shall consist of multiple evaporators using PID control, and Daikin VRV LIFE model condensing unit.

      - The RXSQ condenser shall be a nominal 2 ton, 3 ton, 4 ton or 5 ton direct expansion (DX), air-cooled heat pump air-conditioning system with inverter driven variable speed compressor using R-410A refrigerant.

      - The condensing unit may connect an indoor evaporator capacity up to 130% of the condensing unit capacity.  All zones are each capable of operating separately with individual temperature control.

      - The Daikin condensing unit shall be interconnected to indoor unit models CXTQ, FXFQ, FXHQ, FXUQ, FXEQ, FXMQ, FXLQ, FXNQ, FXTQ, FXDQ, FXZQ, and FXAQ and shall range in capacity from 5,800 Btu/h to 60,000 Btu/h in accordance with Daikin’s engineering data book detailing each available indoor unit.

        - The indoor units shall be connected to the condensing unit utilizing Daikin’s REFNET™ specified piping joints and headers to ensure correct refrigerant flow and balancing.  T style joints are not acceptable for a variable refrigerant system.

      - Operation of the system shall permit either cooling or heating of all of the indoor units.  Each indoor unit or group of indoor units shall be able to provide set temperature independently via a local navigation remote controller (BRC1E73), an Intelligent Touch Controller (ITC) or an Intelligent Tough Manager (ITM).

      - The RXSQ condensing unit model numbers and the associated number of connectable indoor units per RXSQ condensing unit is indicated in the following table.  Each indoor unit or group of indoor units shall be independently controlled.

| MODEL NUMBER | NOMINAL CAPACITY (Tons) | MAXIMUM NUMBER OF INDOOR UNITS |
| --- | --- | --- |
| RXSQ24TBVJ* | 2 | 4 |
| RXSQ36TBVJ* | 3 | 6 |
| RXSQ48TBVJ* | 4 | 8 |
| RXSQ60TBVJ* | 5 | 9 |

    - VRV LIFE FEATURES AND BENEFITS

      - Gas Furnace Connectivity – Heat Pump condensing units shall be connectable to Daikin Communicating gas furnaces with AFUE ranging from 80% to 97%

      - Advanced Zoning - A single heat pump system shall provide for up to 9 zones.

      - Flexible Indoor Unit selection - A single heat pump system shall provide flexibility to choose from one of the various configurations provided below

        - 1 to 1 combination – A single heat pump condensing unit shall provide for connection to 1 indoor unit, where in the indoor unit may be either a VRV Indoor unit or a VRV A-coil (CXTQ) paired with allowable Daikin Communicating gas furnace

        - 1 to 2 combination – A single heat pump condensing unit shall provide for connection to 2 indoor units, where in

          - both the indoor units may be VRV Indoor units or

          - both indoor units may be VRV A-coils (CXTQs) paired with allowable Daikin Communicating gas furnaces or

          - 1 indoor unit may be VRV Indoor unit and another indoor unit may be a VRV A-coil (CXTQ) paired with allowable Daikin Communicating gas furnace

        - 1 to multi combination - A single heat pump condensing unit shall provide for connection to 2 or more indoor units depending on the maximum number of allowable indoor units provided in table under section 2.02.A.7.

      - Choice of Indoor Units – A single heat pump system shall provide the capability to connect a combination of ducted and duct-free indoor units

      - Voltage Platform - Heat pump condensing units shall be available with a 208-230V/1ph/60Hz power supply.

      - Independent Control - Each indoor unit shall use a dedicated electronic expansion valve for independent control.

      - VFD Inverter Control - Each condensing unit shall use high efficiency, variable speed all “inverter” compressor(s) coupled with inverter fan motors to optimize part load performance. Compressor capacity shall be modulated automatically to maintain a constant suction pressure, while varying the refrigerant volume for the needs of the cooling or heating loads.

        - Indoor shall use PID to control superheat to deliver a comfortable room temperature condition.

      - Variable Refrigerant Temperature (VRT) Control – Each condensing unit shall utilize an algorithm to automatically adjust the refrigerant suction and condensing temperature in response to the heating and cooling loads, and in response to the current weather conditions.  The VRT control shall be capable of being customized in the following models and sub-modes:

        - Automatic (factory preset) – The Automatic VRT mode shall allow the target evaporator temperature (Te) and target condensing temperature (Tc) to float based on outdoor ambient temperature conditions, and shall incorporate the following sub-modes:

          - Powerful

          - Quick

          - Mild (factory preset)

        - High Sensible – The High Sensible mode shall allow the system Te and Tc valves to be programmed to series of fixed Te and Tc values.  The High Sensible mode shall also be capable of incorporating the following sub-modes:

          - Eco

        - Basic – The basic mode shall disable the VRT control of the outdoor unit and allow the system to operate with constant Te and Tc values.

      - Flexible Design –(For 4 and 5 ton units)

        - Systems shall be capable of up to 125ft (38m) of linear piping between the condensing unit and furthest located indoor unit.

        - Systems shall be capable of up to 492ft (150 m) total “one-way” piping in the piping network.

        - Systems shall have a vertical (height) separation of up to 49ft (15m) between the condensing unit and the indoor units.

        - Systems shall be capable of up to 100ft (30.5 m) from the first joint / branch point.

        - The condensing unit shall have the ability to connect an indoor unit evaporator capacity of up to 130% of the condensing unit nominal capacity.

      - Flexible Design –(For 2 and 3 ton units)

        - Systems shall be capable of up to 125ft (38 m) of linear piping between the condensing unit and furthest located indoor unit.

        - Systems shall be capable of up to 328ft (100 m) total “one-way” piping in the piping network.

        - Systems shall have a vertical (height) separation of up to 33ft between the condensing unit and the indoor units.

        - Systems shall be capable of up to 100ft (30.5 m) from the first joint / branch point.

        - The condensing unit shall have the ability to connect an indoor unit evaporator capacity of up to 130% of the condensing unit nominal capacity.

      - Simple wiring – Systems shall use 16/18 AWG, 2 wire, stranded, non-shielded and non-polarized daisy chain control wiring.

      - Space saving – Each system shall have a condensing unit module footprint of the following dimensions:

        - RXSQ24TBVJ*: 39”H x 37”W x 12-5/8”D

        - RXSQ36TBVJ*: 39”H x 37”W x 12-5/8”D

        - RXSQ48TBVJ*: 39”H x 37”W x 12-5/8”D

        - RXSQ60TBVJ*: 52-15/16”H x 35-7/16”W x 12-5/8”D

      - Advanced diagnostics – Systems shall include a self-diagnostic, auto-check function to detect a malfunction and display the type and location.

      - Advanced controls – Each system shall have at least one remote controller capable of controlling up to 16 indoor units.

      - Auto Balance Point – A single heat pump system shall be capable of calculating the Balance Point temperature depending on the outdoor ambient temperatures and connected indoor unit loads. The balance point shall be calculated such that upon reaching the balance point temperature the heat pump system shall initiate gas furnace heating for the indoor zone served by a VRV A coil and Daikin communicating gas furnace. The remainder of the zones shall be served with heat pump heating

      - Multi-Zone Dual – Fuel – A single heat pump system shall be capable of providing simultaneous heat pump and gas furnace heat when connected with 1 or more indoor units such that, zones served by VRV indoor units deliver heat pump heat and zone served by Daikin communicating gas furnace provide either heat pump or gas furnace heating only.

      - Ease of Installation – A single VRV heat pump system, upon making appropriate onsite field setting programming; shall be capable of delivering performance as calculated using engineering manuals when interconnecting refrigerant lines sizes are of larger diameter than sizes recommended by Daikin.

      - Un-insulated Liquid line – A single VRV heat pump system, when used in replacement applications and upon making appropriate onsite field setting programming; shall be operational where the main liquid line may be uninsulated

    - PERFORMANCE:

      - The VRV LIFE, RXSQ_TA system shall be rated in accordance with AHRI 210/240 test conditions as show in the performance table below:

| System | Combined with | Nominal Cooling Capacity | EER2 | SEER2 | Nominal Heating Capacity | COP | Low Heating Capacity | COP | HSPF2 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Btu/hr | 95°F |  | Btu/hr | 47°F | Btu/hr | 17°F |  |
| RXSQ24TBVJ* | Non-Ducted | 24,000 | 14.30 | 18.0 | 27,000 | 4.50 | 14,000 | 2.79 | 8.8 |
|  | Ducted |  | 11.20 | 15.9 |  | 3.35 | 16,800 | 2.45 | 8.2 |
|  | Mixed |  | 12.75 | 17.0 |  | 3.93 | 15,400 | 2.62 | 8.5 |
| RXSQ36TBVJ* | Non-Ducted | 36,000 | 12.00 | 18.2 | 40,000 | 4.10 | 23,600 | 3.00 | 9.0 |
|  | Ducted |  | 9.20 | 15.3 |  | 3.25 | 24,600 | 2.55 | 8.5 |
|  | Mixed |  | 10.60 | 16.8 |  | 3.68 | 24,200 | 2.78 | 8.8 |
| RXSQ48TBVJ* | Non-Ducted | 48,000 | 10.30 | 18.6 | 52,000 | 4.00 | 32,200 | 3.00 | 8.5 |
|  | Ducted |  | 7.90 | 14.6 |  | 3.30 | 30,200 | 2.55 | 8.3 |
|  | Mixed |  | 9.10 | 16.6 |  | 3.65 | 31,200 | 2.78 | 8.4 |
| RXSQ60TBVJ* | Non-Ducted | 57,500 | 9.80 | 18.6 | 57,000 | 4.30 | 37,000 | 3.20 | 8.5 |
|  | Ducted |  | 8.50 | 15.5 |  | 3.50 | 36,400 | 2.65 | 8.5 |
|  | Mixed |  | 9.15 | 17.1 |  | 3.90 | 36,800 | 2.93 | 8.5 |

      - Performance Conditions:

        - Cooling:  Indoor temperature of 80°FDB (26.7°CDB), 67°FWB (19.5°CWB) and outdoor temperature of 95°FDB (35°CDB).

        - Heating:  Indoor temperature of 70°FDB (21.1°CDB) and outdoor temperature of 47°FDB (8.3°CDB), 43°FWB (6.1°CDB).

        - Equivalent piping length: 25ft (7.5m)

      - Cooling Operation:

        - The operating range in cooling will be 23°F DB ~ 122°F DB (-5°CDB ~ 50°CDB).

        - Cooling mode indoor room temperature range will be 57-77°FWB (14°C - 25°CWB).

      - Heating Operation:

        - The heat pump operating range in heating will be -5°F WB – 60°F WB (-20°CWB – 15.5°CWB).

        - Heating mode indoor room temperature range will be 59°FDB - 80°F DB (15°CDB – 26.7°CDB).

  - EQUIPMENT

    - ELECTRICAL:

      - The power supply to the condensing unit shall be:

| POWER SUPPLY VOLTAGE | VOLTAGE RANGE |
| --- | --- |
| 208-230V / 1ph / 60 Hz | 187V – 253V (±10%) |

| MODEL | MCA | MOP | COMPRESSOR RLA |
| --- | --- | --- | --- |
| RXSQ24TBVJ* | 16.5 | 20 | 15.3 |
| RXSQ36TBVJ* | 16.5 | 20 | 15.3 |
| RXSQ48TBVJ* | 29.1 | 35 | 19.0 |
| RXSQ60TBVJ* | 29.1 | 35 | 23.2 |

    - WIRING:

      - The control voltage between the indoor and condensing unit shall be 18VDC non-shielded, stranded 2 conductor cable.

      - The control wiring shall be a two-wire multiplex transmission system, making it possible to connect multiple indoor units to one condensing unit with one 2-cable wire, thus simplifying the wiring installation.

      - The control wiring maximum lengths shall be as shown below:

|  | MAXIMUM WIRING LENGTH | TOTAL WIRING LENGTH |
| --- | --- | --- |
| CONTROL WIRING LENGTH | 984 ft (300 m) | 1,968 ft (600 m) |
| WIRE TYPE | 18 AWG, 2 wire, non-polarity, non-shielded, stranded |  |

    - REFRIGERANT PIPING:

      - RXSQ24TBVJ* (2 ton model) and RXSQ36TBVJ* (3 ton model):

        - The system shall be capable of refrigerant piping up to 100ft (30.5 m) actual or 125ft (128 m) equivalent from the condensing unit to the furthest indoor unit, a total combined liquid line length of 328ft (99 m) of piping between the condensing and indoor units.

        - The system shall be capable of 98ft (30m) maximum vertical difference, without any oil traps or additional components and 33ft (10m) vertical separation between indoor units on the same system.

      - RXSQ48TBVJ* (4 ton model) and RXSQ60TBVJ* (5 ton model):

        - The system shall be capable of refrigerant piping up to 100ft (30.5 m) actual or 125ft (128 m) equivalent from the condensing unit to the furthest indoor unit, a total combined liquid line length of 492ft (150 m) of piping between the condensing and indoor units.

        - The system shall be capable of 98ft (30m) maximum vertical difference, without any oil traps or additional components and 49ft (15m) vertical separation between indoor units on the same system.

    - PAINT/CORROSION RESISTANCE:

      - Paint and corrosion resistance shall be at a minimum per the table below:

| COMPONENT | VRV IVS |  |  |
| --- | --- | --- | --- |
|  | BASE MATERIAL | SURFACE TREATMENT | COATING THICKNESS |
|  |  |  | External & Internal Surface |
| External Panel Base | Hot-dipped Zinc-coated steel | POLYESTER | N/A |
| External Front Panel | Hot-dipped Zinc-coated steel | POLYESTER | N/A |
| Pillar |  |  |  |
| Compressor Cover | ASTM material | Resin Paint | N/A |
| Fin Guard | Iron wire | Resin Paint | 0.2-0.6mm |
| Fin Guard and Drum | Polypropylene | No treatment required | N/A |
| Fan | Acrylonitrile - glass | No treatment required | N/A |
| Fan Motor Frame | Resin | No treatment required | N/A |
| Fan Motor Shaft | Carbon steel | No treatment required | N/A |
| Fan Motor Support | Hot-dipped Zinc-coated steel | No treatment required |  |
| Heat Exchanger (Fin Only) | Aluminum | Hydrophilic Treatment, Blue | Hydrophilic: 1.05-1.2 g/m2 Anti-corrosion: 0.25-0.3 g/m2 |
| Electrical parts Box | Hot-dip zinc-coated steel | No treatment required | N/A |
| Electrical Parts Board | Glass cloth / Glass nonwoven cloth material | Insulation Varnish | No specific thickness |
| Screws | C tight cup screw M5 | High corrosion resistance treatment | N/A |

  - OUTDOOR/CONDENSING UNIT

    - GENERAL:

      - The condensing unit is designed specifically for use with VRV series components.

      - The condensing unit shall be factory assembled and pre-wired with all necessary electronic and refrigerant controls.

      - The refrigeration circuit of the condensing unit shall consist of Daikin swing compressor, motors, fans, condenser coil, electronic expansion valves, solenoid valves, 4-way valve, distribution headers, capillaries, filters, shut off valves, oil separators, service ports and refrigerant accumulator.

      - Liquid and suction lines must be individually insulated between the condensing and indoor units.

      - The condensing unit can be wired and piped with access from the left, right, rear or bottom.

      - The connection ratio of indoor units to condensing unit shall be permitted up to 130% of nominal capacity.

      - The condensing system shall be able to support the connection of up to 9 indoor units dependent on the model of the condensing unit.

      - The sound pressure level standard shall be that value as listed in the Daikin engineering manual for the specified models at 3 feet from the front of the unit.  The condensing unit shall be capable of operating automatically at further reduced noise during night time.

      - The system will automatically restart operation after a power failure and will not cause any settings to be lost, thus eliminating the need for reprogramming.

      - The condensing unit shall allow for side-by-side installation with minimum spacing as provided in installation manual.

      - The following safety devices shall be included on the condensing unit; high pressure switch, low pressure sensor, control circuit fuses, crankcase heaters, fusible plug, overload relay, inverter overload protector, thermal protectors for compressor and fan motors, over current protection for the inverter and anti-recycling timers.

      - To ensure the liquid refrigerant does not flash when supplying to the various indoor units, the circuit shall be provided with a sub-cooling feature.

      - Oil recovery cycle shall be automatic occurring 2 hours after start of operation and then every 8 hours of operation.

      - The condensing unit shall be capable of heating operation at 0°F (-18°C) dry bulb ambient temperature without additional low ambient controls.

    - UNIT CABINET:

      - The condensing unit shall be completely weatherproof and corrosion resistant.  The unit shall be constructed from rust-proofed mild steel panels coated with a baked enamel finish.

    - FAN:

      - The condensing unit fan(s) shall consist of propeller type, direct-drive 70 or 200 W fan motors that have multiple speed operation via a DC (digitally commutating) inverter.  Reference table below.

| MODEL NUMBER | FAN MOTOR OUTPUT (W) & QUANTITY |
| --- | --- |
| RXSQ24TBVJ* | 200 x 1 |
| RXSQ36TBVJ* | 200 x 1 |
| RXSQ48TBVJ* | 200 x 1 |
| RXSQ60TBVJ* | 70 x 2 |

      - The fan shall be a horizontal discharge configuration with a nominal airflow maximum range of 2,682 CFM to 3,741 CFM dependent on model specified.

      - The fan motor shall have inherent protection and permanently lubricated bearings and be mounted.

      - The fan motor shall be provided with a fan guard to prevent contact with moving parts.

    - SOUND:

      - Nominal sound pressure levels shall be as shown below.

| MODEL NUMBER | SOUND PRESSURE LEVEL dB(A) COOLING / HEATING MODES |
| --- | --- |
| RXSQ24TBVJ* | 58 / 61 |
| RXSQ36TBVJ* | 58 / 61 |
| RXSQ48TBVJ* | 58 / 61 |
| RXSQ60TBVJ* | 57 / 59 |

    - CONDENSER COIL:

      - The condenser coil shall be manufactured from copper tubes expanded into aluminum fins to form a mechanical bond.

      - The heat exchanger coil shall be of a waffle louver fin and rifled bore tube design to ensure high efficiency performance.

      - The heat exchanger on the condensing units shall be manufactured from Hi-X seamless copper tube.

      - The fins shall be coated with an anti-corrosion acrylic resin and hydrophilic film type E1.

      - The condensing unit shall be factory equipped with condenser coil guards.

    - COMPRESSOR:

      - The Daikin inverter swing compressor shall be variable speed (PAM inverter) controlled which is capable of changing the speed to follow the variations in total cooling and heating load as determined by the suction gas pressure as measured in the condensing unit.

        - In addition, samplings of evaporator and condenser temperatures shall be made so that the high/low pressures detected are read every 20 seconds and calculated.  With each reading, the compressor capacity (INV frequency) shall be controlled to eliminate deviation from target value.

      - The inverter driven compressors in the condensing unit shall be of highly efficient reluctance DC (digitally commutating), hermetically sealed swing type.

      - Neodymium magnets shall be adopted in the rotor construction to yield a higher torque and efficiency in the compressor instead of the normal ferrite magnet type.

        - At complete stop of the compressor, the neodymium magnets will position the rotor into the optimum position for a low torque start.

      - The capacity control range shall be 14% to 100%.

      - Each compressor shall be equipped with a crankcase heater, high pressure safety switch, and internal thermal overload protector.

      - Oil separators shall be standard with the equipment together with an intelligent oil management system.

      - The compressor shall be spring mounted to avoid the transmission of vibration eliminating the standard need for spring insolation.

      - Compressor configurations:

| MODEL NUMBER | COMPRESSOR MOTOR OUTPUT (W) | QUANTITY | COMPRESSOR TYPES |
| --- | --- | --- | --- |
| RXSQ24TBVJ* | 1,900 | 1 | Inverter controlled |
| RXSQ36TBVJ* | 1,900 | 1 | Inverter controlled |
| RXSQ48TBVJ* | 3,000 | 1 | Inverter controlled |
| RXSQ60TBVJ* | 3,500 | 1 | Inverter controlled |

  - INDOOR/EVAPOTATOR UNITS

*INSERT AS REQUIRED

- EXECUTION

*INSERT AS REQUIRED

APPENDIX A

HVAC EQUIPMENT ALTERNATE (GENERAL INFORMATION)

- The alternate equipment supplier shall provide to the bidding mechanical contractor a complete equipment data package.

  - This package shall include, but is not limited to, equipment capacities at the design condition, power requirements, indoor units CFM/static pressures, fan curves, installation requirements, and physical dimensions.  Nominal performance data is not acceptable.

  - The mechanical contractor shall request and receive the equipment data package 15 days prior to bid date and submit this package with the alternate bid.

  - The mechanical contractor shall list the equipment supplier and submit the required data package with the bid detailing a complete comparison of the proposed alternate equipment to the specified equipment and the associated cost reduction of the alternate equipment. The contractor bids an alternate manufacturer with full knowledge that that manufactures product may not be acceptable or approved.

  - All equipment must have visible and permanent label clearly identifying the original manufacturer of the equipment. These labels shall have original manufacturer’s name and contact information and be located both inside and outside the equipment and on all equipment-related literature. Submittals shall include the above statement as confirmation by supplier that all conditions are agreed to and complied to. Failure to comply with these requirements shall be sufficient cause for rejection of the submittal and product with no further consideration.

- The alternate equipment supplier shall furnish a complete drawing package to the mechanical contractor 15 days prior to bid day for bidding and installation.

  - The drawing format shall be .dxf or equivalent, on 30"x42" sheets.

  - The HVAC and electrical series design documents will be made available in electronic format for use by the equipment supplier in preparing their drawings.

  - The alternate equipment supplier shall prepare the following drawings:

    - XXX	HVAC Floor Plan

    - XXX	HVAC Refrigerant Piping Plan

    - XXX	HVAC Refrigerant Piping/Controls Details

    - XXX	HVAC Details

    - XXX	HVAC Schedules

  - The alternate equipment supplier shall draft all piping circuits, components, overall building control schematic, detailed control wiring diagrams, system details and schedules for their system.  The drawings shall convey all requirements to successfully install the alternate equipment suppliers system.

  - Provide (2) drawing package sets plotted on 20 lb. vellum.  Provide (1) drawing package in electronic format (.dxf files) on CD.

  - The submitted documents shall be complete system designs and show no less information than the HVAC equipment/controls contract bid documents.

- The equipment supplier shall submit, as part of the equipment data package, condensing unit data sheets.  Data sheets to include the following:

  - COOLING capacities at project design conditions:

    - Cooling (Btu/h)

    - Cooling Input Power (kW)

    - SEER2

    - EER2

  - HEATING capacities at project design conditions:

    - Heating (Btu/h)

    - Heating Input Power (Btu/h)

  - The submitted capacity and efficiency performance must meet or exceed the listed performance on the schedule at the designed outdoor ambient and indoor space temperature conditions including de-rate factors for defrost and refrigerant piping lengths.

    - HSPF2

    - COP

    - OPERATING TEMPERATURE RANGE:

      - Cooling

      - Heating

    - POWER SUPPLY:

      - Maximum Circuit Amps (MCA)

      - Maximum Overcurrent Protection Amps (MOP)

      - Maximum Starting Current (MSC)

      - Condenser Fan Motor

    - REFRIGERANT:

      - Refrigerant type and charge details including field charge for piping to ensure code compliance.

      - Control of refrigerant temperature based on weather and load or alternative function.

    - UNIT DATA:

      - Max. number of indoor units

      - Sound pressure level at 3ft (dBA)

      - Weight (lbs)

      - Dimensions

- The equipment supplier shall guarantee the performance of their system and all published data submitted.  Performance shall be based on the design criteria below.

  - Room Temperature (Cooling)

  - Room Temperature (Heating)

  - Ambient Temperature (Summer)

  - Ambient Temperature (Winter)

- The alternate equipment supplier shall submit with bid, indoor unit data sheets.  Data sheets to include the following:

  - Capacities at project design conditions:

    - Cooling (Btu/h)

    - Heating (Btu/h)

    - Air Flow (CFM)

    - SEER2

    - EER2

    - HSPF2

    - COP

  - External Static Pressure (ESP)

  - Electrical Data (MAC, MOP, MSC, RLA)

  - Weight (lbs)

  - Dimensions