Daikin North America LLC

HVAC Guide Specifications

Multiple Evaporator, Direct Expansion (DX), Water-Cooled, Variable Capacity, Split System

Section 15700 – Mechanical HVAC

Size Range:

8 to 36 Tons Nominal

Daikin Model Numbers:

RWEQ72TBTJ*

RWEQ96TBTJ*

RWEQ120TBTJ*

RWEQ144TBTJ*

RWEQ192TBTJ* (2 x RWEQ96TBTJ*)

RWEQ216TBTJ* (RWEQ96TBTJ* + RWEQ120TBTJ*)

RWEQ240TBTJ* (2 x RWEQ120TBTJ*)

RWEQ264TBTJ* (RWEQ120TBTJ* + RWEQ144TBTJ*)

RWEQ288TBTJ* (2 x RWEQ144TBTJ*)

RWEQ312TBTJ* (2 x RWEQ96TBTJ* + RWEQ120TBTJ*)

RWEQ336TBTJ* (RWEQ96TBTJ* + 2 x RWEQ120TBTJ*)

RWEQ360TBTJ* (3 x RWEQ120TBTJ*)

RWEQ384TBTJ* (2 x RWEQ120TBTJ* + RWEQ144TBTJ*)

RWEQ408TBTJ* (RWEQ120TBTJ* + 2 x RWEQ144TBTJ*)

RWEQ432TBTJ* (3 x RWEQ144TBTJ*)

Part 1 – GENERAL

VARIABLE REFRIGERANT VOLUME (VRV T-Series WC) AIR CONDITIONING

SPECIFICATION – Two Pipe Heat Pump

  - SYSTEM DESCRIPTION

The variable capacity heat pump air conditioning system shall be a Daikin Variable Refrigerant Volume system as specified.  The system shall consist of multiple evaporators using PID control, connected to a single condenser unit or multiple condenser units.  The condenser shall be a direct expansion (DX), water-cooled, heat pump multi-zone air-conditioning system, with inverter driven variable speed compressor(s), using R-410A refrigerant. The condenser shall be a unified heat pump and heat recovery system to allow for future system reconfiguration.  The condensing unit may connect an indoor evaporator capacity up to 150% of the condensing unit capacity.  All indoor units are each capable of operating separately with individual temperature control.

The Daikin condensing unit shall be interconnected to indoor unit models FXFQ, FXHQ, FXMQ, FXLQ, FXNQ, FXTQ, FXDQ, FXZQ, FXAQ, FXUQ, FXEQ and FXMQ_MF and shall range in capacity from 5,800 Btu/h to 96,000 Btu/h in accordance with Daikin’s engineering data book detailing each available indoor unit.  The indoor units shall be connected to the condensing unit utilizing Daikin’s REFNET™ specified piping joints and headers to ensure correct refrigerant flow and balancing. T style joints are not acceptable for a variable refrigerant system.

For heat pump systems, operation of the system shall permit either cooling or heating of all indoor units. Each indoor unit or group of indoor units shall be able to provide set temperature independently via a local remote controller, an Intelligent Touch Controller, an Intelligent Touch Manager or a BMS interface.

The RWEQ condensing unit model numbers and the associated number of connectable indoor units per RWEQ condensing unit are indicated in the following table.  Each indoor unit or group of indoor units shall be independently controlled.

| Model Number | Nominal Capacity (Tons) | Number of Connectable Indoor Units |
| --- | --- | --- |
| RWEQ72TBTJ* | 6 | 12 |
| RWEQ96TBTJ* | 8 | 16 |
| RWEQ120TBTJ* | 10 | 20 |
| RWEQ144TBTJ* | 12 | 25 |
| RWEQ192TBTJ* | 16 | 33 |
| RWEQ216TBTJ* | 18 | 37 |
| RWEQ240TBTJ* | 20 | 41 |
| RWEQ264TBTJ* | 22 | 45 |
| RWEQ288TBTJ* | 24 | 49 |
| RWEQ312TBTJ* | 26 | 54 |
| RWEQ336TBTJ* | 28 | 58 |
| RWEQ360TBTJ* | 30 | 62 |
| RWEQ384TBTJ* | 32 | 64 |
| RWEQ408TBTJ* | 34 | 64 |
| RWEQ432TBTJ* | 36 | 64 |

  - VRV T-SERIES WATER COOLED FEATURES AND BENEFITS

- Voltage Platform – Heat pump condensing units shall be available with a 208-230V/3ph/60Hz power supply.

- Advanced Zoning – A single system shall provide for up to 64 zones.

- Independent Control – Each indoor unit shall use a dedicated electronic expansion valve with 2000 positions for independent control.

- VFD Inverter Control and Variable Refrigerant Temperature – Each condensing unit shall use a high efficiency, variable speed “inverter” compressor with gas injection circuit for superior part load performance and heating capacity.

The system capacity and refrigerant temperatures shall be modulated automatically to set suction and condensing pressures while varying the refrigerant volume for the needs of the cooling or heating loads. The control will be automatic and customizable depending on system load and zone load.

If automatic variable refrigerant temperature control is not standard in both heating and cooling operation by an alternate manufacturer a BMS is required to provide the same control functionality.

Indoor units shall use PID control to control superheat to deliver a comfortable room temperature condition and optimize efficiency.

- Flexible Design –

  - Systems shall be capable of up to 540ft (623 equivalent) of linear piping between the condensing unit and furthest located indoor unit.

  - Systems shall be capable of up to 980ft of total “one-way” piping in the piping network.

  - Systems shall have a vertical (height) separation of up to 164ft between the condensing unit and the indoor units.

  - Systems shall be capable of up to 295ft of linear piping from the first REFNET™ / branch point.

  - The condensing unit shall connect an indoor unit evaporator capacity up to 150% of the condensing unit nominal capacity.

  - Systems shall be capable of 98ft vertical separation between indoor units.

  - System shall be capable of connection to the T-series branch selector boxes (BSQ_T / BS_Q54T).

- Outside Air – Systems shall provide outside air integration capability.

- Space Saving – Each system shall have a condensing unit module footprint no larger than H: 38-9/16” x W: 30-1/8” x D: 22-1/16”. Condensing unit design shall allow for stacking of up to three units to maximize space saving.

- Advanced Diagnostics – Systems shall include a self-diagnostic, auto-check function to detect a malfunction and display the type and location

- Variable Water Flow Control – The system shall be equipped with variable water flow control logic as standard and control water flow by sending 2-9V DC output signal to flow control valve or inverter pump. The system shall be able to be configured as a constant water flow or variable flow system through field settings. If automatic variable water flow control is not available by an alternate manufacturer a BMS is required to provide the same control functionality.

- Each condensing unit shall incorporate contacts for integration of a mandatory flow proving device.

- Heat Rejection Cancellation - The system shall be equipped with heat rejection technology. An internal DX type inverter cooler shall provide cooling for all internal cabinet components, minimizing mechanical room conditioning requirements.

If this feature is not provided by an alternate manufacturer, the contractor shall be responsible to take the necessary measures to air-condition the mechanical room.

- Drop-down Electrical Box - The electrical box shall be hinged and allow access to key internal components without fully disassembling the outer casing.

- Flexible and Easy Installation – Field selectable top or front side refrigerant connections shall be available for each unit.

- Configurator Software - Each system shall be available with configurator software package to allow for remote configuration of operational settings and also for assessment of operational data and error codes.

If this software is not provided by an alternate manufacturer, for each individual condensing unit the contractor shall do the settings manually and keep detailed records for future maintenance purposes.

- Autocharging - Each system shall have a refrigerant auto-charging function.

- Each condensing unit shall incorporate contacts for electrical demand shedding.

- Simple Wiring – Systems shall use 16/18 AWG, 2 wire, stranded, non-shielded and non-polarized daisy chain control wiring.

- Advanced Controls – Each system shall have at least one remote controller capable of controlling up to 16 indoor units.

Each system shall be capable of integrating with open protocol BACnet and LonWorks building management systems.

- Low Sound Pressure Levels – Each system shall use indoor units with quiet operation as low as 28 dB(A) and condensing units as low as 54 dB(A).

  - QUALITY ASSURANCE

- The units shall be tested by a Nationally Recognized Testing Laboratory (NRTL), in accordance with ANSI/UL 1995 – Heating and Cooling Equipment and bear the Listed Mark.

- All wiring shall be in accordance with the National Electric Code (NEC).

- The system will be produced in an ISO 9001 and ISO 14001 facility, which are standards set by the International Standard Organization (ISO).  The system shall be factory tested for safety and function.

- The condensing unit will be factory charged with R-410A.

  - DELIVERY, STORAGE AND HANDLING

- Unit shall be stored and handled according to the manufacturer’s     recommendations.

Part 2 – WARRANTY

STANDARD LIMITED WARRANTY

Complete warranty details available from your local Daikin representative or at www.daikincomfort.com.

Daikin North America LLC warrants original owner of the non-residential building, multifamily residence or residence in which the Daikin products are installed that under normal use and maintenance for comfort cooling and conditioning applications such products (the “Products”) will be free from defects in material and workmanship. This warranty applies to compressor and all parts and is limited in duration to ten (10) years starting from the ‘’installation date’’ which is one of the two dates below:

- The installation date is the date that the unit is originally commissioned, but no later than 18 months after the manufacture date noted on the unit’s rating plate.

- If the date the unit is originally commissioned cannot be verified, the installation date is three months after the manufacture date.

Part 3 – PERFORMANCE

  - The VRV T-Series Water Cooled RWEQ condensing unit shall perform as indicated below:

| Model Number | System IEER* (part load - ducted) | System IEER* (part load – non-ducted) | System IEER* (part load - mixed) |
| --- | --- | --- | --- |
| RWEQ96TATJ* | 25.40 | 30.80 | 28.10 |
| RWEQ120TATJ* | 23.50 | 29.40 | 26.45 |
| RWEQ144TATJ* | 19.80 | 24.30 | 22.05 |
| RWEQ192TATJ* | 24.70 | 26.80 | 25.75 |
| RWEQ216TATJ* | 23.80 | 26.30 | 25.05 |
| RWEQ240TATJ* | 22.70 | 25.90 | 24.30 |
| RWEQ264TATJ* | 20.00 | 23.50 | 21.75 |
| RWEQ288TATJ* | 18.80 | 20.90 | 19.85 |
| RWEQ312TATJ* | 21.80 | 21.90 | 21.85 |
| RWEQ336TATJ* | 21.40 | 21.50 | 21.45 |
| RWEQ360TATJ* | 20.20 | 21.20 | 20.70 |
| RWEQ384TATJ* | 17.90 | 19.50 | 18.70 |
| RWEQ408TATJ* | 17.20 | 18.20 | 17.70 |
| RWEQ432TATJ* | 16.60 | 17.00 | 16.80 |

| Model Number | System EER* (full load - ducted) | System EER* (full load – non-ducted) | System EER* (full load - mixed) |
| --- | --- | --- | --- |

| RWEQ96TATJ* | 15.40 | 19.60 | 17.50 |
| --- | --- | --- | --- |
| RWEQ120TATJ* | 13.60 | 16.00 | 14.80 |
| RWEQ144TATJ* | 12.60 | 15.60 | 14.10 |
| RWEQ192TATJ* | 14.60 | 16.50 | 15.55 |
| RWEQ216TATJ* | 13.80 | 15.00 | 14.40 |
| RWEQ240TATJ* | 12.80 | 14.00 | 13.40 |
| RWEQ264TATJ* | 12.10 | 13.50 | 12.80 |
| RWEQ288TATJ* | 11.50 | 13.10 | 12.30 |
| RWEQ312TATJ* | 12.70 | 13.70 | 13.20 |
| RWEQ336TATJ* | 12.30 | 13.50 | 12.90 |
| RWEQ360TATJ* | 11.70 | 12.40 | 12.05 |
| RWEQ384TATJ* | 11.00 | 12.00 | 11.50 |
| RWEQ408TATJ* | 10.70 | 11.10 | 10.90 |
| RWEQ432TATJ* | 10.30 | 10.50 | 10.40 |

| Model Number | System COP (full load - ducted) | System COP (full load – non-ducted) | System COP (full load - mixed) |
| --- | --- | --- | --- |
| RWEQ96TATJ* | 5.80 | 6.27 | 6.04 |
| RWEQ120TATJ* | 5.55 | 6.10 | 5.83 |
| RWEQ144TATJ* | 5.33 | 6.01 | 5.67 |
| RWEQ192TATJ* | 5.82 | 5.82 | 5.82 |
| RWEQ216TATJ* | 5.68 | 5.68 | 5.68 |
| RWEQ240TATJ* | 5.49 | 5.52 | 5.51 |
| RWEQ264TATJ* | 4.98 | 5.34 | 5.16 |
| RWEQ288TATJ* | 4.92 | 5.30 | 5.11 |
| RWEQ312TATJ* | 4.86 | 5.50 | 5.18 |
| RWEQ336TATJ* | 4.73 | 5.42 | 5.08 |
| RWEQ360TATJ* | 4.70 | 5.30 | 5.00 |
| RWEQ384TATJ* | 4.12 | 4.53 | 4.33 |
| RWEQ408TATJ* | 4.03 | 4.35 | 4.19 |
| RWEQ432TATJ* | 3.92 | 4.19 | 4.06 |

Performance Rated in accordance with AHRI1230

All tested values surpass the minimum efficiency levels regulated in the DOE Code of Federal Regulation 10 CFR Ch. II § 431.97.

There is no minimum efficiency defined in 10 CFR Ch. II § 431.97 for Water Cooled Packaged equipment greater than 135,000 Btu/hr.

3.02	OPERATING RANGE

Cooling mode indoor room temperature range will be 57°F-77°F WB.

Heating mode indoor room temperature range will be 59°F-80°F DB.

Ambient operating range for the condensing unit shall be between 35-104°F DB and 80% RH or lower (non-condensing).

STANDARD OPERATING RANGE

Inlet water temperature (cooling/heating):  50 - 113°F.

GEOTHERMAL OPERATING RANGE

Inlet water temperature (cooling): 23 - 113°F.

Inlet water temperature (heating): 14 - 95°F.

Note: antifreeze and application rules must be followed

3.03	REFRIGERANT PIPING

The system shall be capable of refrigerant piping up to 540 feet actual (or 623 feet equivalent) from the condensing unit to the furthest indoor unit, a total combined liquid line length of 980 feet of piping between the condensing and fan coil units with up to 164 feet maximum vertical difference, without any oil traps or additional components.

REFNET™ piping joints and headers shall be used to ensure proper refrigerant balance and flow for optimum system capacity and performance. T style joints shall not be acceptable as this will negatively impact proper refrigerant balance and flow for optimum system capacity and performance.

3.04	DESIGN BASIS

The HVAC equipment basis of design is Daikin North America.  All bidders shall furnish the minimum system standards as defined by the base bid model numbers, model families or as otherwise specified herein (see Key General Specifications Alternate Supplier Checklist).  In any event, the contractor shall be responsible for all specified items and intents of this document without further compensation.

Part 4 – PRODUCTS

  - CONDENSING UNIT

- General:  The condensing unit is designed specifically for use with VRV T-Series Water Cooled components.

  - The condensing unit shall be factory assembled and pre-wired with all necessary electronic and refrigerant controls.

  - The refrigeration circuit of the condensing unit shall consist of Daikin inverter scroll compressors with gas injection circuit, motors, brazed plate heat exchanger, electronic expansion valves, solenoid valves, 4-way valve, fans, distribution headers, capillaries, filters, shut off valves, oil separators, service ports, liquid receivers and refrigerant accumulator.

  - Discharge pressure gas line, liquid and suction lines must be individually insulated between the condensing and indoor units.

  - The connection ratio of indoor units to condensing unit shall be permitted up to 150% of nominal capacity, dependent on the model of the condensing unit and connected indoor units.

  - Each condensing system shall be able to support the connection of up to 64 indoor units, dependent on the model of the condensing unit.

  - System shall have an operable flow rate range of 13.2 – 39.6 gpm per module for standard operation and 21.2 – 39.6 gpm for geothermal operation.

  - System shall have an operating inlet water temperature range of 50°F-113°F for standard operation and down to 23F in cooling and 14F in heating for geothermal operation.

  - The sound pressure level standard shall be that value as listed in the Daikin engineering manual for the specified models at 3.3 feet from the front of the unit.

| Model Number | Sound Pressure Level dB(A) |
| --- | --- |
| RWEQ96TATJ* | 54 |
| RWEQ120TATJ* | 55 |
| RWEQ144TATJ* | 60.5 |
| RWEQ192TATJ* | 57 |
| RWEQ216TATJ* | 57.5 |
| RWEQ240TATJ* | 58 |
| RWEQ264TATJ* | 61.5 |
| RWEQ288TATJ* | 63.5 |
| RWEQ312TATJ* | 59 |
| RWEQ336TATJ* | 59.5 |
| RWEQ360TATJ* | 60 |
| RWEQ384TATJ* | 62 |
| RWEQ408TATJ* | 64 |
| RWEQ432TATJ* | 65 |

  - The system will automatically restart operation after a power failure and will not cause any settings to be lost, thus eliminating the need for reprogramming.

  - Each condensing unit shall have a 220VAC, 3mA-0.5A control circuit output for water pump or isolation valve operation.  This circuit shall be configured at commissioning to operate based on system or compressor operation.

  - Each condensing unit shall incorporate normally open, 15VDC and 1.0mA rated contacts for integration of a mandatory flow proving device.

  - Each condensing unit shall incorporate contacts for electrical demand shedding from a central BMS, utility control or demand meter.

  - The condensing unit shall be modular in design and should allow for side-by-side or stacked (dual/triple) installation with minimum spacing.

  - The following safety devices shall be included on the condensing unit; high pressure sensor and switch, low pressure sensor, control circuit fuses, crankcase heater, fusible plug, overload relay, inverter overload protector, thermal protector for compressor motor, over current protection for the inverter, anti-recycling timer and heater exchanger freeze protection.

  - To ensure the liquid refrigerant does not flash when supplying to the various indoor units, the circuit shall be provided with a sub-cooling feature.

  - Oil recovery cycle shall be automatic occurring 2 hours after start of operation and then every 8 hours of operation.

- Unit Cabinet:

- The condensing unit shall be corrosion resistant.  The unit shall be constructed from rust-proofed, mild steel panels coated with a baked enamel finish.

- Condenser Heat Exchanger:

- The condenser heat exchanger shall be a stainless brazed plate type designed for closed loop/dry cooler applications. Coaxial type heat exchangers shall not be acceptable.

- The heat exchanger shall use 1-1/4” FPT inlet piping.

- The heat exchanger shall use 1-1/4” FPT outlet piping.

- The heat exchanger shall use 3/8” FPS drain piping.

- The heat exchanger shall have a maximum system water pressure of 464 psi.

- Strainer shall be provided as a standard accessory to be installed on the inlet of the condenser.

- Compressor:

  - The Daikin inverter Flash Vapor injection scroll compressors shall be variable speed (PVM inverter) controlled which is capable of changing the speed to follow the variations in total cooling and heating load as determined by the suction gas pressure as measured in the condensing unit.  In addition, samplings of evaporator and condenser temperatures shall be made so that the high/low pressures detected are read every 20 seconds and calculated.  With each reading, the compressor capacity (INV frequency) shall be controlled to eliminate deviation from target value. Non–inverter-driven compressors, which may cause starting motor current to exceed the nominal motor current (RLA) and require larger wire sizing, shall not be allowed.

  - The inverter driven compressor in each condensing unit shall be of highly efficient reluctance DC (digitally commutating), hermetically sealed scroll “K-type”.

  - Neodymium magnets shall be adopted in the rotor construction to yield a higher torque and efficiency in the compressor instead of the normal ferrite magnet type.  At complete stop of the compressor, the neodymium magnets will position the rotor into the optimum position for a low torque start.

  - The capacity control range shall be as low as 4% to 100%.

  - Each compressor shall be equipped with a crankcase heater, high pressure safety switch, and internal thermal overload protector.

  - Oil separators shall be standard with the equipment together with an intelligent oil management system.

  - The compressor shall be mounted on vibration dampening rubber grommets to minimize the transmission of vibration, eliminating the standard need for external spring isolation.

  - Units sized 8-12 ton shall contain 1 compressor, 16-24 ton units shall contain 2 compressors and 26-36 ton units shall contain 3 compressors.  In the event of compressor failure the remaining compressors shall continue to operate and provide heating or cooling as required at a proportionally reduced capacity.  The microprocessor and associated controls shall be designed to specifically address this condition for single module and manifold systems.

  - In the case of multiple condenser modules, operation hours of the compressors shall be balanced by means of the Duty Cycling Function, ensuring sequential starting of each module at each start/stop cycle or every 8 hours.

  - Compressor configurations:

| Model Number | Number of Compressors | Compressor Types (hermetically sealed scroll) |
| --- | --- | --- |
| RWEQ96TATJ* | 1 | Inverter controlled |
| RWEQ120TATJ* | 1 | Inverter controlled |
| RWEQ144TATJ* | 1 | Inverter controlled |
| RWEQ192TATJ* | 2 | All inverter controlled |
| RWEQ216TATJ* | 2 | All inverter controlled |
| RWEQ240TATJ* | 2 | All inverter controlled |
| RWEQ264TATJ* | 2 | All inverter controlled |
| RWEQ288TATJ* | 2 | All inverter controlled |
| RWEQ312TATJ* | 3 | All inverter controlled |
| RWEQ336TATJ* | 3 | All inverter controlled |
| RWEQ360TATJ* | 3 | All inverter controlled |
| RWEQ384TATJ* | 3 | All inverter controlled |
| RWEQ408TATJ* | 3 | All inverter controlled |
| RWEQ432TATJ* | 3 | All inverter controlled |

- Electrical:

  - The power supply to the condensing unit shall be 208/230 volts, 3 phase, 60 hertz +/- 10%.

| Power Supply Voltage | Total Voltage |
| --- | --- |
| 208-230V/3/60 | 187V-253V |

| Model | MCA | MOP | Compressor RLA |
| --- | --- | --- | --- |
| RWEQ96TATJ* | 28.8 | 35 | 19 |
| RWEQ120TATJ* | 36.5 | 45 | 20.9 |
| RWEQ144TATJ* | 44.6 | 50 | 29.4 |
| RWEQ192TATJ* | 28.8 + 28.8 | 35 + 35 | 19 + 19 |
| RWEQ216TATJ* | 28.8 + 36.5 | 35 + 45 | 19 + 20.9 |
| RWEQ240TATJ* | 36.5 + 36.5 | 45 + 45 | 20.9 + 20.9 |
| RWEQ264TATJ* | 36.5 + 44.6 | 45 + 50 | 20.9 + 29.4 |
| RWEQ288TATJ* | 44.6 + 44.6 | 50 + 50 | 29.4 + 29.4 |
| RWEQ312TATJ* | 28.8 + 28.8 + 36.5 | 35 + 35 + 45 | 19 + 19 + 20.9 |
| RWEQ336TATJ* | 28.8 + 36.5 + 36.5 | 35 + 45 + 45 | 19 + 20.9 + 20.9 |
| RWEQ360TATJ* | 36.5 + 36.5 + 36.5 | 45 + 45 + 45 | 20.9 + 20.9 + 20.9 |
| RWEQ384TATJ* | 36.5 + 36.5 + 44.6 | 45 + 45 + 50 | 20.9 + 20.9 + 29.4 |
| RWEQ408TATJ* | 36.5 + 44.6 + 44.6 | 45 + 50 + 50 | 20.9 + 29.4 + 29.4 |
| RWEQ432TATJ* | 44.6 + 44.6 + 44.6 | 50 + 50 + 50 | 29.4 + 29.4 + 29.4 |

  - The control voltage between the indoor and condensing unit shall be 16VDC non-shielded, stranded 2 conductor cable.

  - The control wiring shall be a two-wire multiplex transmission system, making it possible to connect multiple indoor units to one condensing unit with one 2-cable wire, thus simplifying the wiring operation.

  - The control wiring lengths shall be as shown below.

|  | Condenser to Indoor Unit | Condenser to Central Controller | Indoor Unit to Remote Control |
| --- | --- | --- | --- |
| Control Wiring Length | 6,665 ft | 3,330 ft | 1,665 ft |
| Wire Type | 16/18 AWG, 2 wire, non-polarity, non-shielded, stranded |  |  |

  - VRV INDOOR UNITS

* INSERT INDOOR UNITS AS REQUIRED

Part 5 - HVAC EQUIPMENT ALTERNATE (GENERAL INFORMATION)

5.01	The alternate equipment supplier shall provide to the bidding mechanical contractor a complete equipment data package.  This package shall include, but is not limited to, equipment capacities at the design condition, power requirements, indoor units CFM/static pressures, fan curves, installation requirements, and physical dimensions.  Nominal performance data is not acceptable.

The mechanical contractor shall request and receive the equipment data package 15 days prior to bid date and submit this package with the alternate bid.

The mechanical contractor shall list the equipment supplier and submit the required data package with the bid detailing a complete comparison of the proposed alternate equipment to the specified equipment and the associated cost reduction of the alternate equipment. The contractor bids an alternate manufacturer with full knowledge that the manufacturer’s product may not be acceptable or approved.

5.02	The alternate equipment supplier shall furnish a complete drawing package to the mechanical contractor 15 days prior to bid day for bidding and installation. The drawing format shall be .dxf or equivalent, on 30"x42" sheets.  The HVAC and electrical series design documents will be made available in electronic format for use by the equipment supplier in preparing their drawings. The alternate equipment supplier shall prepare the following drawings:

XXX	HVAC Floor Plan
XXX	HVAC Refrigerant Piping Plan

XXX	HVAC Refrigerant Piping/Controls Details

XXX	HVAC Details

XXX	HVAC Schedules

The alternate equipment supplier shall draft all piping circuits, components, overall building control schematic, detailed control wiring diagrams, system details and schedules for their system.  The drawings shall convey all requirements to successfully install the alternate equipment suppliers system.

Provide (2) drawing package sets plotted on 20 lb. vellum.  Provide (1) drawing package in electronic format (.dxf files) on CD.

The submitted documents shall be complete system designs and show no less information than the HVAC equipment/controls contract bid documents.

5.03  	The equipment supplier shall submit as part of the equipment data package condensing unit data sheets.  Data sheets to include the following:

Cooling Capacities at project design conditions:

Cooling (Btu/h)

Cooling Input Power – ducted (kW)

Cooling Input Power – ductless (kW)

Cooling Input Power – mixed (kW)

Part Load IEER – ducted

Part Load IEER – ductless

Part Load IEER – mixed

Full Load EER – ducted

Full Load EER – ductless

Full Load EER - mixed

Heating Capacities at project design conditions:

Heating (Btu/h)

Heating Input Power – ducted (kW)

Heating Input Power – ductless (kW)

Heating Input Power – mixed (kW)

Full Load COP– ducted

Full Load COP– ductless

Full Load COP – mixed

The submitted capacity and efficiency performance must meet or exceed the listed performance on the schedule at the designed flow rate, EWT and space conditions including de-rate factors for defrost if applicable and refrigerant piping losses.

Operating Temperature Range:

Cooling

Heating

Flow Rate per Module

(gpm)

Variable water flow control logic which can be configured as a constant water flow or variable flow system through field settings.

Pressure Drop

(psi)

Power Supply:

Maximum Circuit Amps (MCA)

Maximum Overcurrent Protection Amps (MOP)

Maximum Starting Current (MSC)

Refrigerant:

Refrigerant type and charge details including field charge for piping to ensure code compliance.

Control of refrigerant temperature based on load or alternative function.

Unit Data:

Max. Number of Indoor Units

Sound Pressure Level at 3ft. (dBA)

Weight (lbs)

Dimensions

5.04	The equipment supplier shall guarantee the performance of their system and all published data submitted.  Performance shall be based on the design criteria below.

Room Temperature (Cooling):  ________________________________

Room Temperature (Heating):  ________________________________

Inlet Water Temperature (Summer):  __________________________

Inlet Water Temperature (Winter):  ____________________________

Flow Rate per Module:  _____________________________________

Refrigerant Piping Loss: _____________________________________

5.05	The alternate equipment supplier shall submit with bid, indoor unit data sheets.  Data sheets to include the following:

Capacities at project design conditions:

Cooling (Btu/h)

Cooling Input Power (kW)

Part Load IEER

Full Load EER

Heating (Btu/h)

Heating Input Power (kW)

Full Load COP

External Static Pressure (ESP)

Electrical Data (MCA, MOP, MSC, RLA)

Weight (lbs)

Dimensions